## macchine
|  | Internal combustion Engine | [9 empty] | N units | 1
| Size (fuel max) | 2500 | kW | 0.14409 | 0.42521 | [8 empty] | vincoli dinamici |  |  |  | 4984.1715
| Load min (Fmin/Fmax) | 0.5 |  |  |  |  | F | P | Q | eta_el | eta_th | eta_1 | PES | rampa up | no vincolo
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0.49 | convex hull |  | vertex min | 1250 | 441.17 | 531.93 | 0.35294 | 0.42554 | 0.77848 | 0.15161 | min up time | 6h
|  | k2P | -0.017 |  |  | vertex max | 2500 | 1053.67 | 1080.68 | 0.42147 | 0.43227 | 0.85374 | 0.24428 | start-up cost | 0.076959 | extra fuel input at max load | 2500
|  | k3P | -128.83 | [10 empty] | O&M | 0
[6 empty] | m-el | 0.49 | [6 empty] | Capital cost | 1053670
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.439 |  |  | q-el | -171.33 | [6 empty] | Maintenance cost
|  | k2Q | -0.05 |  |  | m-th | 0.439
|  | k3Q | 108.18 |  |  | q-th | -16.82
|  | Boiler 1 | [9 empty] | N units | 2
| Size (fuel max) | 2500 | kW | 0.32533 | [9 empty] | vincoli dinamici
| Load min (Fmin/Fmax) | 0.25 |  |  |  |  | F | P | Q | eta_el | eta_th |  |  | rampa up | no vincolo
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0 | convex hull |  | vertex min | 625 | 0 | 530 | 0 | 0.848 |  |  | min up time | 2h
|  | k2P | 0 |  |  | vertex max | 2500 | 0 | 2360 | 0 | 0.944 |  |  | start-up cost | 0.050355 | extra fuel input at max load
|  | k3P | 0 | [10 empty] | O&M | 0
[14 empty] | Capital cost | 173400
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.976 | [10 empty] | Maintenance cost | 3468
|  | k2Q | -0.032 |  |  | m-th | 0.976
|  | k3Q | 0 |  |  | q-th | -80
|  | ORC small | [9 empty] | N units | 0 | 0
| Size (fuel max) | 0 | kW | 1094 | 3651 | fuel | [7 empty] | vincoli dinamici
| Load min (Fmin/Fmax) | 0.37 |  |  |  |  | F | P | Q | eta_el | eta_th |  |  | rampa up | 25%/ora
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0.133 | convex hull |  | vertex min | 0 | -5.125 | -14.4 | #DIV/0! | #DIV/0! |  |  | min up time | 24h
|  | k2P | -0.01049 |  |  | vertex max | 0 | -5.125 | -14.4 | #DIV/0! | #DIV/0! |  |  | start-up cost | 0.1 | extra fuel input at max load
|  | k3P | -5.125 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.6214
|  | k2Q | 0.04225
|  | k3Q | -14.4
|  | ORC large | [9 empty] | N units | 0
| Size (fuel max) | 3814 | kW | 3651 | 31787 | fuel | [7 empty] | vincoli dinamici
| Load min (Fmin/Fmax) | 0.37 |  |  |  |  | F | P | Q | eta_el | eta_th |  |  | rampa up | 25%/ora
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0.1536 | convex hull |  | vertex min | 1411.18 | 145.4418 | 1007.0546 | 0.10306 | 0.71363 |  |  | min up time | 24h
|  | k2P | -0.0111 |  |  | vertex max | 3814 | 514.515 | 2572.2515 | 0.1349 | 0.67442 |  |  | start-up cost | 0.1 | extra fuel input at max load
|  | k3P | -28.98 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.6514
|  | k2Q | 0.02585
|  | k3Q | -10.78
|  | HEAT PUMP | [9 empty] | N units | 1 | 0
| Size (elec input max) | 500 | kW | 0.23933 | [9 empty] | vincoli dinamici
| Load min (Fmin/Fmax) | 0.13 |  |  |  |  | F | P | Q |  | COP |  |  | rampa up | no vincolo
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0 | convex hull |  | vertex min | 65 | 0 | 193.35 | 0 | 2.9746 |  |  | min up time | no vincolo
|  | k2P | 0 |  |  | vertex max | 500 | 0 | 1755 | 0 | 3.51 |  |  | start-up cost | 0.11864 | extra electric power input at full load
|  | k3P | 0 | [10 empty] | O&M | 0
[14 empty] | Capital cost | 595450
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 3.59 | [10 empty] | Maintenance cost | 8931.75
|  | k2Q | -0.08 |  |  | m-th | 3.59
|  | k3Q | 0 |  |  | q-th | -40
|  | THERMAL STORAGE | [9 empty] | N units |  | 1
| heat loss | 0.005 | of current storage level
| size (max capacity) | 2000 | kWh
|  | BATTERY | [9 empty] | N units |  | 0
| size (max capacity) | 0
| discharge efficiency | 0.97
| charge efficiency | 0.97
|  | THERMAL SOLAR PANELS | [9 empty] | N units |  | 1
| Surface of panels | xxx | m2
| peak power | 1000 | kW
|  | PV SOLAR PANELS | [9 empty] | N units |  | 1
| Surface of panels | xxx | m2
| peak power | 1000 | kW
|  | BIOMASS BOILER | [9 empty] | N units |  | 0
| Size (fuel max) | 0 | kW
| Load min (Fmin/Fmax) | 0.25 |  |  |  |  | F | P | Q | eta_el | eta_th |  |  | rampa up | 50%
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0 | convex hull |  | vertex min | 0 | 0 | 0 | #DIV/0! | #DIV/0! |  |  | min up time | 4h
|  | k2P | 0 |  |  | vertex max | 0 | 0 | 0 | #DIV/0! | #DIV/0! |  |  | start-up cost | 0.1 | extra fuel input at max load
|  | k3P | 0 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.87
|  | k2Q | -0.03
|  | k3Q | 0
|  | BOILER 2 | [9 empty] | N units |  | 0
| Size (fuel max) | 55 | kW
| Load min (Fmin/Fmax) | 0.25 |  |  |  |  | F | P | Q | eta_el | eta_th |  |  | rampa up | no vincolo
performance map: Pel= k1*F+k2*S+k3 |  | k1P | 0 | convex hull |  | vertex min | 13.75 | 0 | 11.66 | 0 | 0.848 |  |  | min up time | 2h
|  | k2P | 0 |  |  | vertex max | 55 | 0 | 51.92 | 0 | 0.944 |  |  | start-up cost | 0.050355 | extra fuel input at max load
|  | k3P | 0 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q | 0.976
|  | k2Q | -0.032
|  | k3Q | 0
|  | REFRIFERATION CYCLE | [9 empty] | N units |  | 0
| Size (Pel IN max) | 100 | kW | load_chage_slope | 0.36
| Load min (Fmin/Fmax) | 0.11 |  |  |  |  | P | Qref _1 |  | COP |  |  |  | rampa up | no vincolo
tratto 1: performance map: qref= k1*Pel+k2*S+k3 |  | k1P | 11.1027 | convex hull |  | vertex min | 11 | 89.7397 |  | 8.1582 |  |  |  | min up time | no vincolo
|  | k2P | -0.3239 |  |  | vertex mid | 36 | 367.3072 |  | 10.203 |  |  |  | start-up cost | 0 | extra fuel input at max load
|  | k3P | 0 |  |  | vertex max | 100 | 610 |  | 6.1 |  |  |  | O&M | 0
tratto 2: performance map: qref= k1*Pel+k2*S+k3 |  | k1Q | 3.8055
|  | k2Q | 2.2945
|  | k3Q | 0
|  | ABSORPTION REF CYCLE | [9 empty] | N units |  | 0
| Size (Qin thermal max) | 2200 | kW
| Load min (Fmin/Fmax) | 0.2 |  |  |  |  | QIN | Qref |  | COP |  |  |  | rampa up | no vincolo
performance map: Qref= k1*QIN+k2*S+k3 |  | k1P | 0.78 | convex hull |  | vertex min | 440 | 343.2 |  | 0.78 |  |  |  | min up time | 0
|  | k2P | 0 |  |  | vertex max | 2200 | 1716 |  | 0.78 |  |  |  | start-up cost | 0 | extra fuel input at max load
|  | k3P | 0 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q
k2Q
k3Q
|  | ABSORPTION REF CYCLE | [9 empty] | N units |  | 0
| Size (Qin thermal max) | 3100 | kW
| Load min (Fmin/Fmax) | 0.2 |  |  |  |  | QIN | Qref |  | COP |  |  |  | rampa up | no vincolo
performance map: Qref= k1*QIN+k2*S+k3 |  | k1P | 0.78 | convex hull |  | vertex min | 620 | 483.6 |  | 0.78 |  |  |  | min up time | 0
|  | k2P | 0 |  |  | vertex max | 3100 | 2418 |  | 0.78 |  |  |  | start-up cost | 0 | extra fuel input at max load
|  | k3P | 0 | [10 empty] | O&M | 0
performance map: Q= k1*F+k2*S+k3 |  | k1Q
k2Q
k3Q